The Wilkins Reduced Pressure Back Flow that is in the yard ‘appears’ to be supplied from a take-off on the inlet side of the riser stack.

Note: - There is no Back Flow Preventer on the riser flange before the valve stack. - There is a mech-T take-off to the lawn irrigation system via a Wilkins 5-75PRV 4” OS&Y

Confirmed: This line goes to outside lawn irrigation sprinks. Is this line metered? Utility water bypassing meters. Wilkins 50-75psi PRV Victaulic 4” grooved Orbit lawn sprinkler controller Data required: need clear ‘Calc’ card photos

PVC line from Fire Riser to Lawn sprinks

|  | The lawn sprinkler Zurn-Wilkins model 375 RP, “appears” to be supplied via a tap-off from the fire suppression riser stack. Please investigate. |
| --- | --- |

This may be a Code violation.