The Wilkins Reduced Pressure Back Flow that is in the yard ‘appears’ to be supplied from a take-off on the inlet side of the riser stack.

|  |
| --- |
| C:\Users\Owner\AppData\Local\Microsoft\Windows\INetCache\Content.Word\20190829_Riser valve 4inch OS&Y.JPG  **Note:**   1. There is no Back Flow Preventer on the riser flange before the valve stack. 2. There is a mech-T take-off to the lawn irrigation system via a Wilkins 5-75PRV   4” OS&Y |

|  |
| --- |
| C:\Users\Owner\AppData\Local\Microsoft\Windows\INetCache\Content.Word\20190829_Riser Valve Stack Victaulic 4inch Grv Check.jpg  **Confirmed:** This line goes to outside lawn irrigation sprinks.  Is this line metered? Utility water bypassing meters.  Wilkins 50-75psi PRV  Victaulic 4” grooved  Orbit lawn sprinkler controller  **Data required:** need clear ‘Calc’ card photos |

**PVC line from Fire Riser to Lawn sprinks**

|  |
| --- |
|  |
|  |

|  |  |
| --- | --- |
|  | |
|  | The lawn sprinkler Zurn-Wilkins model 375 RP, “appears” to be supplied via a tap-off from the fire suppression riser stack.  Please investigate. |
|  |  |
|  |  |

This may be a Code violation.