Hydrant distances from FDC?

No riser door signs. IS riser room lit, and heated?

Alarm panel and ?annunciator?

Antifreeze system has had additions to it. 2022 limit per State Fire Marshal, along with: this is a Care Center, will prohibit the permissibility of an extension. Additions and alterations to this building may require site brought up to current Code.

Tap off the fire system water supply is not permitted. See Public Utilities water. (metering)

See Code re: riser water supply to irrigation.

Calc Card. 2011 by State Fire for Art city Nursing

These were observed 2019-08-29

Antifreeze: Top of loop

Antifreeze loop: top of closet to ceiling above

Antifreeze loop mid

Antifreeze loop bottom of loop

Antifreeze addition in attic with workers as at 2019-08-20

Stop work order on door

Work in progress on roof 2019-08-20. Not AF line.

Temp Fire clearance expired.

State FM Deficiencies report -2 pages

New addition to Antifreeze system